## Slide 1: Pipe Networks
Pipeline systems
  Transmission lines
  Pipe networks
  Measurements
  Manifolds and diffusers
  Pumps
  Transients
You are here

## Slide 2: Pipeline systems: Pipe networks
Water distribution systems for municipalities
Multiple sources and multiple sinks connected with an interconnected network of pipes.
Computer solutions!
  KYpipes
  WaterCAD
  CyberNET
  EPANET
http://www.epa.gov/ORD/NRMRL/wswrd/epanet.html

## Slide 3: Water Distribution System Assumption
Each point in the system can only have one _______
The pressure change from 1 to 2 by path a must equal the pressure change from 1 to 2 by path b
a
b
1
2
pressure
Same for path b!

## Slide 4: Water Distribution System Assumption
a
b
1
2
Pressure change by path a
Pipe diameters are constant or K.E. is small
Model withdrawals as occurring at nodes so V is constant between nodes
Or sum of head loss around loop is _____.
zero
(Need a sign convention)

## Slide 5: Pipes in Parallel
A
B
Q1
Qtotal
energy
proportion
Find discharge given pressure at A and B
  ______& ____ equation
  add flows
Find head loss given the total flow
  assume a discharge Q1’ through pipe 1
  solve for head loss using the assumed discharge
  using the calculated head loss to find Q2’
  assume that the actual flow is divided in the same _________ as the assumed flow
Q2
S-J

## Slide 6: Networks of Pipes
____ __________ at all nodes
The relationship between head loss and discharge must be maintained for each pipe
  Darcy-Weisbach equation
    _____________
  Exponential friction formula
    _____________
A
0.32 m3/s
0.28 m3/s
?
b
a
1
2
Mass conservation
Swamee-Jain
Hazen-Williams

## Slide 7: Network Analysis
Find the flows in the loop given the inflows and outflows.
The pipes are all 25 cm cast iron (e=0.26 mm).
A
B
C
D
0.10 m3/s
0.32 m3/s
0.28 m3/s
0.14 m3/s
200 m
100 m

## Slide 8: Network Analysis
Assign a flow to each pipe link
Flow into each junction must equal flow out of the junction
A
B
C
D
0.10 m3/s
0.32 m3/s
0.28 m3/s
0.14 m3/s
0.32
0.00
0.10
0.04
arbitrary

## Slide 9: Network Analysis
Calculate the head loss in each pipe
f=0.02 for Re>200000
k1,k3=339
k2,k4=169
A
B
C
D
0.10 m3/s
0.32 m3/s
0.28 m3/s
0.14 m3/s
1
4
2
3
Sign convention +CW

## Slide 10: Network Analysis
The head loss around the loop isn’t zero
Need to change the flow around the loop
  the ___________ flow is too great (head loss is positive)
  reduce the clockwise flow to reduce the head loss
Solution techniques
  Hardy Cross loop-balancing (___________ _________)
  Use a numeric solver (Solver in Excel) to find a change in flow that will give zero head loss around the loop
  Use Network Analysis software (EPANET)
clockwise
optimizes correction

## Slide 11: Numeric Solver
Set up a spreadsheet as shown below.
the numbers in bold were entered, the other cells are calculations
initially Q is 0
use “solver” to set the sum of the head loss to 0 by changing Q
the column Q0+ Q contains the correct flows

## Slide 12: Solution to Loop Problem
A
B
C
D
0.10 m3/s
0.32 m3/s
0.28 m3/s
0.14 m3/s
0.218
0.102
0.202
0.062
1
4
2
3
Q0+ DQ
0.218
-0.062
-0.202
-0.102
Better solution is software with a GUI showing the pipe network.

## Slide 13: Network Elements
Controls
  Check valve (CV)
  Pressure relief valve
  Pressure reducing valve (PRV)
  Pressure sustaining valve (PSV)
  Flow control valve (FCV)
Pumps: need a relationship between flow and head
Reservoirs: infinite source, elevation is not affected by demand
Tanks: specific geometry, mass conservation applies

## Slide 14: Check Valve
Valve only allows flow in one direction
The valve automatically closes when flow begins to reverse
closed
open

## Slide 15: Pressure Relief Valve
Valve will begin to open when pressure in the pipeline ________ a set pressure (determined by force on the spring).
pipeline
closed
relief flow
open
exceeds
Low pipeline pressure
High pipeline pressure
Where high pressure could cause an explosion (boilers, water heaters, …)

## Slide 16: Pressure Regulating Valve
Valve will begin to open when the pressure ___________ is _________ than the setpoint pressure (determined by the force of the spring).
sets maximum pressure downstream
closed
open
less
downstream
High downstream pressure
Low downstream pressure
Similar function to pressure break tank

## Slide 17: Pressure Sustaining Valve
Valve will begin to open when the pressure ________ is _________ than the setpoint pressure (determined by the force of the spring).
sets minimum pressure upstream
closed
open
upstream
greater
Low upstream pressure
High upstream pressure
Similar to pressure relief valve

## Slide 18: Flow control valve (FCV)
Limits the ____ ___ through the valve to a specified value, in a specified direction
Commonly used to limit the maximum flow to a value that will not adversely affect the provider’s system
flow rate

## Slide 19: Pressure Break Tanks
In the developing world small water supplies in mountainous regions can develop too much pressure for the PVC pipe.
They don’t want to use PRVs because they are too expensive and are prone to failure.
Pressure break tanks have an inlet, an outlet, and an overflow.
Is there a better solution?

## Slide 20: Network Analysis Extended
The previous approach works for a simple loop, but it doesn’t easily extend to a whole network of loops
Need a matrix method
  Initial guess for flows
  Adjust all flows to reduce the error in pressures
  __________________________
  _______________________________
Simultaneous equations
Appendix D of EPANET manual

## Slide 21: Pressure Network Analysis Software: EPANET
A
B
C
D
0.10 m3/s
0.32 m3/s
0.28 m3/s
0.14 m3/s
0.218
0.102
0.202
0.062
1
4
2
3
junction
pipe
reservoir

## Slide 22: EPANET network solution

## Slide 25: EPANET Emitters