## Slide 1: Hydraulic Transients
When the Steady-State design fails!

## Slide 2: Hydraulic Transients: Overview
In all of our flow analysis we have assumed either _____ _____ operation or ________ ______ flow
What about rapidly varied flow?
  How does flow from a faucet start?
  How about flow startup in a large, long pipeline?
  What happens if we suddenly stop the flow of water through a tunnel leading to a turbine?
steady state
gradually
varied

## Slide 3: Hydraulic Transients
Routine transients
  change in valve settings
  starting or stopping of pumps
  changes in power demand for turbines
  changes in reservoir elevation
  turbine governor ‘hunting’
  action of reciprocating pumps
  lawn sprinkler
Unsteady Pipe Flow: time varying flow and pressure
Catastrophic transients
  unstable pump or turbine operation
  pipe breaks

## Slide 4: References
Chaudhry, M. H. 1987. Applied Hydraulic Transients. New York, Van Nostrand Reinhold Company.
Wylie, E. B. and V. L. Streeter. 1983. Fluid Transients. Ann Arbor, FEB Press.

## Slide 5: Analysis of Transients
Gradually varied (“Lumped”) _________
  conduit walls are assumed rigid
  fluid assumed incompressible
  flow is function of _____ only
Rapidly varied (“Distributed”) _________
  fluid assumed slightly compressible
  conduit walls may also be assumed to be elastic
  flow is a function of time and ________
ODE
PDE
time
location

## Slide 6: Establishment of Flow: Final Velocity
2
V
EGL
HGL
1
H
L
Ken= ____
Kexit= ____
g = 9.8 m/s2
H = 100 m
K = ____
f = 0.02
L = 1000 m
D = 1 m
1.5
0.5
1.0
major
minor
How long will it take?

## Slide 7: Final Velocity
9.55 m/s
g = 9.8 m/s2
H = 100 m
 K = 1.5
f = 0.02
L = 1000 m
D = 1 m
What would V be without losses? _____
44 m/s

## Slide 8: Establishment of Flow: Initial Velocity
before head loss becomes significant
g = 9.8 m/s2
H = 100 m
 K = 1.5
f = 0.02
L = 1000 m
D = 1 m
0
1
2
3
4
5
6
7
8
9
10
0
5
10
15
20
25
30
time (s)
velocity (m/s)
Navier Stokes?

## Slide 9: Flow Establishment: Full Solution
________, ________
gravity
drag

## Slide 10: Flow Establishment: tanh!
V < Vf

## Slide 11: Time to reach final velocity
Time to reach 0.9Vf increases as:
L increases
H decreases
Head loss decreases

## Slide 12: Flow Establishment
g = 9.8 m/s2
H = 100 m
K = 1.5
f = 0.02
L = 1000 m
D = 1 m
Chart: time (s)
Was f constant?
107

## Slide 13: Household plumbing example
Have you observed the gradual increase in flow when you turn on the faucet at a sink?
  50 psi - 350 kPa - 35 m of head
  K = 10 (estimate based on significant losses in faucet)
  f = 0.02
  L = 5 m (distance to larger supply pipe where velocity change is less significant)
  D = 0.5” - 0.013 m
  time to reach 90% of final velocity?
T0.9Vf = 0.13 s
No?
Good!

## Slide 14: V > Vf?
Chart: time (s)
If V0=
Why does velocity approach final velocity so rapidly?

## Slide 15: Lake Source Cooling Intake Schematic
Intake Pipe, with flow Q and cross sectional area Apipe
Wet Pit, with plan view area Atank
Lake Water Surface
?
Steel Pipe
100 m
Plastic Pipe
3100 m
Pump inlet
length of intake pipeline is 3200 m
1 m
Motor
What happens during startup?
What happens if pump is turned off?

## Slide 16: Transient with varying driving force
H = ______________________________
Lake elevation - wet pit water level
f(Q)
Finite Difference Solution!
Q
where
What is z=f(Q)?
Is f constant?

## Slide 17: Wet Pit Water Level and Flow Oscillations
constants
What is happening on the vertical lines?
-2
-1.5
-1
-0.5
0
0.5
1
1.5
2
0
200
400
600
800
1000
1200
time (s)
Q (m
3
/s)
-4
-3
-2
-1
0
1
2
3
4
z (m)
Q
z

## Slide 18: Wet Pit with Area Equal to Pipe Area
Pipe collapse
Water Column Separation
Why is this unrealistic?

## Slide 19: Overflow Weir at 1 m

## Slide 20: Period of Oscillation: Frictionless Case
z = -H
Wet pit mass balance
z = 0 at lake surface

## Slide 21: Period of Oscillations
plan view area of wet pit (m2) 24
pipeline length (m) 3170
inner diameter of pipe (m) 1.47
gravity (m/s2) 9.81
T = 424 s
Pendulum Period?

## Slide 22: Transients
In previous example we assumed that the velocity was the same everywhere in the pipe
We did not consider compressibility of water or elasticity of the pipe
In the next example water compressibility and pipe elasticity will be central

## Slide 23: Valve Closure in Pipeline
V
Sudden valve closure at t = 0 causes change in discharge at the valve
What will make the fluid slow down?____
Instantaneous change would require __________
Impossible to stop all the fluid instantaneously
infinite force
What do you think happens?
↑p at valve

## Slide 24: Transients: Distributed System
Tools
  Conservation of mass
  Conservation of momentum
  Conservation of energy
We’d like to know
  pressure change
    rigid walls
    elastic walls
  propagation speed of pressure wave
  time history of transient

## Slide 25: Pressure change due to velocity change
velocity
density
pressure
unsteady flow
steady flow
HGL

## Slide 26: Momentum Equation
HGL
1
2
Mass conservation
A1  A2
Dp = p2 - p1
Neglect head loss!

## Slide 27: Magnitude of Pressure Wave
1
2
Decrease in V causes a(n) _______ in HGL.
increase

## Slide 28: Propagation Speed: Rigid Walls
Conservation of mass
Solve for DV

## Slide 29: Propagation Speed: Rigid Walls
momentum
mass
Need a relationship between pressure and density!

## Slide 30: Propagation Speed: Rigid Walls
definition of bulk modulus of elasticity
Example:
Find the speed of a pressure wave in a water pipeline assuming rigid walls.
speed of sound in water
(for water)

## Slide 31: Propagation Speed: Elastic Walls
D
t = thickness of thin walled pipe
E = bulk modulus of elasticity for pipe
Additional parameters
D = diameter of pipe
effect of water compressibility
effect of pipe elasticity

## Slide 32: Propagation Speed: Elastic Walls
solution
Example: How long does it take for a pressure wave to travel 500 m after a rapid valve closure in a 1 m diameter, 1 cm wall thickness, steel pipeline? The initial flow velocity was 5 m/s.
E for steel is 200 GPa
What is the increase in pressure?

## Slide 33: Time History of Hydraulic Transients: Function of ...
Time history of valve operation (or other control device)
Pipeline characteristics
  diameter, thickness, and modulus of elasticity
  length of pipeline
  frictional characteristics
    tend to decrease magnitude of pressure wave
Presence and location of other control devices
  pressure relief valves
  surge tanks
  reservoirs

## Slide 34: Time History of Hydraulic Transients
V=Vo
V=0
a
DH
L
V=0
DH
L
V= -Vo
V=0
a
DH
L
V= -Vo
L
1
2
3
4

## Slide 35: Time History of Hydraulic Transients
V= -Vo
V=0
a
DH
L
V=0
DH
L
V=Vo
V=0
a
DH
L
V= Vo
L
5
6
7
8

## Slide 36: Pressure variation over time
reservoir level
Pressure variation at valve: velocity head and friction losses neglected
DH
time
Pressure head
Neglecting head loss!
Real traces

## Slide 37: Lumped vs. Distributed
For LSC wet pit
  T = 424 s
  = 4*3170 m/1400 m/s = ____
pressure fluctuation period
lumped
9.1 s
For _______ system
T = __________________________
What would it take to get a transient with a period of 9 s in Lake Source Cooling? ____________
Fast valve

## Slide 38: Methods of Controlling Transients
Valve operation
  limit operation to slow changes
  if rapid shutoff is necessary consider diverting the flow and then shutting it off slowly
Surge tank
  acts like a reservoir closer to the flow control point
Pressure relief valve
  automatically opens and diverts some of the flow when a set pressure is exceeded

## Slide 39: Surge Tanks
Reservoir
Tunnel/Pipeline
Tail water
T
Penstock
Reduces amplitude of pressure fluctuations in ________ by reflecting incoming pressure waves
Decreases cycle time of pressure wave in the penstock
Start-up/shut-down time for turbine can be reduced (better response to load changes)
Surge tank
tunnel
Surge tanks

## Slide 40: Use of Hydraulic Transients
There is an old technology that used hydraulic transients to lift water from a stream to a higher elevation. The device was called a “Ram Pump”and it made a rhythmic clacking noise.
How did it work?
High pressure pipe
Stream
Ram Pump
Source pipe

## Slide 41: Minimum valve closure time
How would you stop a pipeline full of water in the minimum time possible without bursting the pipe?

## Slide 42: Simplify: no head loss and hold pressure constant
Integrate from 0 to t and from Q to 0 (changes sign)

## Slide 43: Back to Ram Pump: Pump Phase
Coordinate system?
P1 = _____
P2 = _____
z2-z1 = ___
High pressure pipe
Stream
Source pipe
0
z3
z1
z
-z1

## Slide 44: Reflections
What is the initial head loss term if the pump stage begins after steady state flow has been reached? _____
What is ?_____
What is when V approaches zero? ______
Where is most efficient pumping? ___________
How do you pump the most water? ______
z1
z3
Low V (low hl)
Maintain high V

## Slide 45: Ram: Optimal Operation
What is the theoretical maximum ratio of pumped water to wasted water?
Rate of decrease in PE of wasted water equals rate of increase in PE of pumped water

## Slide 46: High Q and Low loses?
Chart: time (s)
Acceleration
Deceleration (pumping)
Insignificant head loss
Keep V high for max Q

## Slide 47: Cycle times
Change in velocities must match

## Slide 48: Summary (exercise)
When designing systems, pay attention to startup/shutdown
Design systems so that high pressure waves never occur
High pressure waves are reflected at reservoirs or surge tanks

## Slide 49: Burst section of Penstock: Oigawa Power Station, Japan
Chaudhry page 17

## Slide 50: Collapsed section of Penstock: Oigawa Power Station, Japan
Chaudhry page 18

## Slide 51: Values for Wet Pit Analysis
Flow rate before pump failure (m3/s) 2
plan view area of wet pit (m2) 24
pipeline length (m) 3170
inner diameter of pipe (m) 1.47
elevation of outflow weir (m) 10
time interval to plot (s) 1000
pipe roughness (m) 0.001
density (kg/m3) 1000
dynamic viscosity (Ns/m2) 1.00E-03
gravity (m/s2) 9.81

## Slide 52: Pressure wave velocity: Elastic Pipeline
E = 200 GPa
D = 1 m
t = 1 cm
0.5 s to travel 500 m

## Slide 53: Ram Pump
Water inlet
Air Chamber
Rapid valve

## Slide 54: Ram pump
High pressure pipe
Stream
Ram Pump
Source pipe
H1
H2

## Slide 55: Ram animation
Notes: http://schou.dk/animation/

## Slide 56: Ram Pump
Time to establish flow
Chart: time (s)

## Slide 57: Surge Tanks

## Slide 58: Real pressure traces
At valve
At midpoint
Notes: http://www.iahr.org/publications/assets/jhr39-3/developments.pdf